## ITP
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 1 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
Customer Name: |  |  |  | Project: |  |  |  | ITP No: |  | Date:
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
A | APPROVAL
A1 | Shop Drawings |  |  |  | Before to start the activity | P | A | A | Approved Shop Drawings
A2 | Method Statements |  |  | Tender Specifications | Before to start the activity | P | A | A | Approved MS
A3 | Equipment & material catalogues including technical engineering documents |  |  | Tender Specifications | Before to start the activity | P | A | A | Approved Catalogues
B | MATERIALS RECEIVING INSPECTION
B1 | Visual Inspection of Cables, Trays, Distribution Boards, MCC Panels, VSD Panels, Sub Switchboards, Canopy Genset including arcoustic equipment, UPS, Busway, SSO, Light Fittings, etc.: - as approved. - no paint/surface coating damages. - no dents, etc. |  |  | Approved Shop Drawings & Accepted Materials | Before Installation | I, P | A | A | RFIT MRIR
C | INSTALLATION MOCK UP
C1 | For on-site installation, mock up to be installed prior to start any new activities. |  |  | Approved Shop/ Mock Up Drawings, Catalogues & Method Statement | Before Installation | I, P | A | A | RFIT
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 2 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
D | INSTALLATION
D1 | Underground cables: - cables laid as per route & procedures. - individual backfill levels as per approved method statement and shop drawing. - cables labelled. - route markers placed. |  |  | Approved Shop/ Mock Up Drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F4/R1
D2 | Compound/Street Lighting: - installed as per drawings. - labelled as per drawings. - Individual backfill levels as per approved method statement. |  |  | Approved Shop/ Mock Up Drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F8/R1
D3 | Busway: - installed as per drawings. - labelled as per drawings. - verify continuity and insulation resistance progressively during installation/coupling. |  |  | Approved Shop Drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT QMS/TRE1
D4 | Electrical Distribution Boards : - installed as per plan/drawings. - damaged wall/floor repaired (if applicable). - touch up paint completed. - labelled correctlly. - earthing connected to board. - cables glands & earthing completed. - cables cores terminated with lugs & ferulled as per drawings. - MCBs/MCCBs installed, labelled & functions checked. |  |  | Approved Shop Drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F5/R1
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 3 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
D4 | Electrical Distribution Boards : - installed as per plan/drawings. - damaged wall/floor repaired (if applicable). - touch up paint completed. - labelled correctlly. - earthing connected to board. - cables glands & earthing completed. - cables cores terminated with lugs & ferulled as per drawings. - MCBs/MCCBs installed, labelled & functions checked. |  |  | Approved Shop Drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F5/R1
D5 | Genset including arcoustic equipment: - installed as per drawings. - labelled as per drawings. |  |  | Approved Shop Drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F12/R1 IC/E/F20/R1
D6 | UPS: - installed as per drawings. - labelled as per drawings. |  |  | Approved Shop drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F11/R1
D7 | LV Cables & cable trays: - installed trays as per approved routes. - trays secured firmly to structure. - repairs to damaged walls, structure, floor, etc. completed. - cable laid & secured with cable ties to trays. - cables & trays labelled as per drawings |  |  | Approved Shop drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F10/R1
D8 | Lightings, Switch Socket Outlets, Switches, etc.: - installed as per drawings. - labelled as per drawings. |  |  | Approved Shop drawings, Catalogues & Method Statement | Before Testing | I, P | A | A | RFIT IC/E/F6/R1 IC/E/F7/R1 IC/E/F8/R1 IC/E/F9/R1
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 4 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
E | PRE-COMMISSIONING
E1 | Underground Cables: - physical inspection. - visual inspection. - terminations as per drawings at both ends. - continuity tested & recorded. - IR tested (ph-ph, ph-earth) & recorded. |  |  | Approved Shop Drawings & Catalogue | Before Commissiong | I, P | A | A | RFIT QMS/TRE1
E2 | Busways / Busducts: - physical Inspection. - visual Inspection. - terminations as per drawings at both ends. - continuity tested & recorded. - IR tested (ph-ph, ph-earth) & recorded. |  |  | Approved Shop Drawings & Catalogue | Before Commissiong | I, P | A | A | RFIT QMS/TRE1
E3 | Electrical Distribution Boards: - physical Inspection. - visual Inspection. - terminations as per drawings at both ends. - cable continuity tested & recorded. - cable IR tested (ph-ph, ph-earth) & recorded. |  |  | Approved Shop Drawings & Catalogue | Before Commissiong | I, P | A | A | RFIT QMS/TRE1
E4 | Genset including arcoustic equipment: - physical Inspection. - visual Inspection. - terminations as per drawings at both ends. - cable continuity tested & recorded. - cable IR tested (ph-ph, ph-earth) & recorded. |  |  | Approved Shop Drawings & Catalogue | Before Commissiong | I, P | A | A | RFIT QMS/TRE1
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 5 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
E5 | UPS: - physical Inspection. - visual Inspection. - terminations as per drawings at both ends. - cable continuity tested & recorded. - cable IR tested (ph-ph, ph-earth) & recorded. |  |  | Approved Shop Drawings & Catalogue | Before Commissiong | I, P | A | A | RFIT QMS/TRE1 Manufacturer's Service Report
E6 | Lighting including Switches, Emergency Lights & Keluar Signs: - physical Inspection. - visual Inspection. |  |  | Approved Shop Drawings, Catalogue & Single Line Drawing | Before Commissiong | I, P | A | A | RFIT PD/ESTR
E7 | Power Sockets: - physical Inspection. - visual Inspection. |  |  | Approved Shop Drawings, Catalogue & Single Line Drawing | Before Commissiong | I, P | A | A | RFIT PD/ESTR
F | Commissioning
F1 | Underground Cables: - physical inspection. - visual inspection. - verify terminations at both ends. - pressure test & recorded. - voltage tested & recorded. |  |  | Approved Shop Drawings & Catalogue | After Pre- Commissiong | I, P | A | A | RFIT QMS/TRE1
F2 | Busways/Busducts: - physical inspection. - visual inspection. - verify terminations at both ends. - contact resistance tested & recorded. - voltage tested & recorded. |  |  | Approved Shop Drawings & Catalogue | After Pre- Commissiong | I, P | A | A | RFIT QMS/TRE1
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 6 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
F3 | Electrical Distribution Boards: - visual Inspection. - verify terminations at both ends. - physical inspection. - functional test. - protection test. - voltage tested & recorded. - phase rotation tested & recorded. |  |  | Approved Shop Drawings & Catalogue | After Pre- Commissiong | I, P | A | A | RFIT QMS/TRE1
F4 | Genset including arcoustic equipment: - physical inspection. - visual inspection. - verify terminations at both ends. - votage tested & recorded. - phase rotation tested & recorded. - ATS functionality tested & recorded. |  |  | Approved Shop Drawings & Catalogue | After Pre- Commissiong | I, P | A | A | RFIT QMS/TRE1 | Note 1
F5 | UPS: - physical inspection. - visual inspection. - verify terminations at both ends. - site functional test. - protection test. - voltage tested & recorded. |  |  | Approved Shop Drawings & Catalogue | After Pre- Commissiong | I, P | A | A | RFIT Manufacturer's Acceptance Certificate
F6 | Lighting including Switches, Emergency Lights & Keluar Signs: - test lighting. - lux level test. |  |  | Approved Shop Drawings, Catalogue & Single Line Drawing | After Pre- Commissiong | I, P | A | A | RFIT QMS/TRE1 IC/E/F23/R1 | Note 1
HEXATECH |  | PROJECT MANAGEMENT |  |  |  | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017 |  | Page 7 of 7
|  | Inspection & Test Plan - General Electrical Works |  |  |  | Revision No.: 0 |  |  |  | Document Ref.: PD-REC-ITPGEW
ITEM | INSPECTION/TEST STAGE |  |  | REQUIREMENT AND ACCEPTANCE CRITERIA | FREQUENCY | ACTION |  |  | INSPECTION RECORD / FORM NO. | NOTES
[6 empty] | HEXATECH | PMC | CLIENT
F7 | Switch Socket Outlets: - test functionality. |  |  | Approved Shop Drawings, Catalogue & Single Line Drawing | After Pre- Commissiong | I, P | A | A | RFIT QMS/TRE1
G | FINAL INSPECTION & ACCEPTANCE
G1 | Final inspection: - punch list cleared. |  |  | 100% | At work completion | I | A | A | Punchlist
G2 | As Built Drawing. |  |  | Approved Shop Drawing, Tender Specs, IFC Drawings | At work completion | P | A | A | TN
G3 | Dossier Compilation & Issuance. |  |  | Handover Requirement | At work completion | P | A | A | TN, CPC, Project Handover Form
| Note 1: BOMBA Inspection |  | Abbreviations: | A | Approval |  |  | RFIT | Request For Inspection & Testing
|  |  |  | R | Review |  |  | MRIR | Material Receiving Inspection Report
|  |  |  | I | Inspection |  |  | TRE1 | Test Report Electrical No. 1
|  |  |  | W | Wittness |  |  | ESTR | Electrical Services Test Report
|  |  |  | P | Prepare Documentation |  |  | MS | Method Statement
|  |  |  | H | Hold |  |  | PD | Project Department
|  |  |  | TN | Transmittal Note |  |  | QMS | Quality Management System
|  |  |  | CPC | Certificate of Project Completion