## HIRARC
HEXATECH ENGINEERING SDN. BHD. |  | OPERATIONS CONTROL SERVICES | [5 empty] | Issue No.: 1 |  | Document Effective Date: 01 Mar 2017
|  | HAZARD IDENTIFICATION, RISK ASSESSMENT & RISK CONTROL CHART | [5 empty] | Rev. No.: 0 |  |  | Document Ref: OCS-REC-HIRARCC
HIRARC MASTER FORM
Company | [5 empty] | HIRARCM NO.:
Process / Location / Project | [5 empty] | DATE:
Approved by MD: | [5 empty] | Prepared by
Project Start Date | [5 empty] | (Name, Designation)
Job Description : General electrical installation
1.Hazard Identification |  |  |  |  | 2. Risk Analysis |  |  |  | 3. Risk Control
No | Work Activity |  | Hazard | Which can cause / effect | Existing Risk Control (if any) | Likelihood | Severity | Risk | Recommended Control Measures |  |  | PIC (Due date & status)
General
1 | Walk around at project site (Project Management team, Visitors) for walkdown, inspection, installation works, commissioning, administrational duties. |  | Gravity | Fall from Height | Using appropriate PPE. Conduct Safety induction and daily toolbox briefing | 1 | 2 | 2
|  |  |  | Slip, Trip and Fall |  | 1 | 2 | 2
|  |  |  | Falling objects |  | 1 | 2 | 2
2 | Working at Height with: |  | Gravity | Fall from Height | Using appropriate PPE | 1 | 2 | 2
| - Ladder |  |  | Falling objects | Use proper 'A' Frame ladder,buddy system | 1 | 2 | 2
| - Mobile scafforld |  |  |  | Training for operating scissor lifts and erection of scaffold.(Certified scaffolder)
- Scaffold
- Scissor Lift
Access site with vehicle
3 | - Lorry |  | Vehicle; Gravity | Being caught between, struck by or against vehicles; Falling objects | Using appropriate PPE, licenced vehicle driver, crane certificate of safe usage. | 1 | 3 | 3
| - Crane |  |  |  |  | 1 | 3 | 3
Loading/Unloading of material/equipment
4 | - Manual handling (lifting / carrying) |  | Manual handling | Muscular Stress | Manual lifting procedure | 2 | 1 | 2
|  |  | Gravity | Slip, Trip and Fall | Look out for trip hazards, such as uneven floors or trailing cables, and implement housekeeping | 1 | 1 | 1
| - Heavy load moving skate / Cargo roller |  | Vehicle; Gravity | Being caught between, struck by or against vehicles; Falling objects | Using appropriate PPE, licenced vehicle driver, crane certificate of safe usage. | 1 | 3 | 3
| - Trolley |  |  |  |  | 1 | 1 | 1
| - Pallet Jack |  |  |  |  | 1 | 1 | 1
| - Fork Lift |  |  |  |  | 2 | 2 | 4
| - Crane |  |  |  |  | 1 | 3 | 3
Cable Support / device installation
5 | Excavation for underground cable incl. laying of sleeve & cable |  | Vehicle | Being caught between, struck by or against vehicles | Barrication, Signage, Backup beeper, Using appropriate PPE | 1 | 3 | 3
|  |  | Gravity | Falling oblects | Using appropriate PPE | 1 | 2 | 2
|  |  | Electrical | Exposure to underground services or overhead electrical cables | Get the location of existing services and brief the team.Assess the site location for any obstructions. | 1 | 3 | 3
|  |  | Confined space | Drowning due to water flooding | Check if the wheather conditions are safe to work, prior to start work. | 1 | 3 | 3
6 | Use of Hand Tools (Hammer, Screw Driver, Plier, Wrench) |  | Electricity | Electric shock due to contact with energized parts | Use of insulated tools, appropriate PPE | 1 | 3 | 3
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
7 | Use of mechanical conduit bender |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
8 | Drilling/hacking in concrete |  | Vibration | Damage to your hands and fingers | Check the condition of anti-vibration mounts etc where fitted. Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Noise | Hearing loss | Using appropriate PPE | 1 | 1 | 1
|  |  | Kinetic Energy | Eye injury from flying debris | Using appropriate PPE | 1 | 2 | 2
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Electrical | Electrical shock due to faulty equipment or power cord. | Tool checklist and tags are implemented. | 1 | 2 | 2
9 | Drilling, grinding & cutting metal |  | Vibration | Damage to your hands and fingers | Check the condition of anti-vibration mounts etc where fitted. Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Noise | Hearing loss | Using appropriate PPE | 1 | 1 | 1
|  |  | Kinetic Energy | Eye injury from flying debris | Using appropriate PPE | 1 | 2 | 2
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Electrical | Electrical shock due to faulty equipment or power cord. | Tool checklist and tags are implemented. | 1 | 2 | 2
|  |  | Fire | Sparks can cause fire. | No flameble material to be near to work area. | 1 | 2 | 2
10 | Welding |  | Noise | Hearing loss | Using appropriate PPE | 1 | 1 | 1
|  |  | Heat | Excessive exposure to hot work environment can cause heat-related illnesses | Whenever possible, scheduling hot jobs for the cooler part of the day. Ensuring that workers are drinking enough water. Adjusting work practices as necessary when workers experience heat stress | 1 | 1 | 1
|  |  | Fire | Sparks and molten metals created by the arc can cause fire. | No flameble material to be near to work area. | 1 | 2 | 2
|  |  | Burns | Sparks and molten metals can cause skin injuries. | Using appropriate PPE | 1 | 3 | 3
|  |  | Electricity | Electrical shock due to contact with material or electrode | Ensure good condition of welding equipment. Welding material to be grounded. | 1 | 2 | 2
|  |  | Ultraviolet Radiation | ultraviolet light causes inflammation of the cornea | Using appropriate PPE | 1 | 2 | 2
|  |  | Toxic fumes and gases | Fume produced during welding have potential health effects | Welding to be done in open area (Outside). Welder to be briefed about health effects of fumes & gases. | 1 | 1 | 1
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
11 | Install support (Trunking, Ladder, Conduit ) at height |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Gravity | Fall from Height; Slip, Trip and Fall; Falling objects | Using appropriate PPE, Safety net if applicable, barrication, signage. | 1 | 2 | 2
|  |  | Ergonomics | Fatiguen Stress and Errors, due to wokplace design. | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Electricity | Electrical shock due to contact with energizes cables in adjacency | Avoid contact with energized equipment, Insulated safety shoes, | 1 | 2 | 2
12 | Install support (Trunking, Ladder or Conduit) below raise floor |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Gravity | Slip, Trip and Fall | Barrication, signage, housekeeping | 1 | 1 | 1
|  |  | Ergonomics | Fatiguen Stress and Errors, due to wokplace design. | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Electricity | Electrical shock due to contact with energizes cables in adjacency | Avoid contact with energized equipment, Insulated safety shoes, | 1 | 2 | 2
Cable installation
13 | Cable cutting (Hydraulic Cable Cutter) |  | Penetrating sharp object | Hand injuries due to wrong handling of tool | Skilled workers to give briefing and to monitor the handling of tools. | 2 | 2 | 4
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work.
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work.
14 | Cable pulling |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Gravity | Fall from Height; Slip, Trip and Fall; Falling objects | Using appropriate PPE, Safety net if applicable | 1 | 2 | 2
|  |  | Ergonomics | Fatiguen Stress and Errors, due to wokplace design. | Provide sufficient breaks during work. | 1 | 2 | 2
15 | Install cable gland (Drill hole into MSB cover plate, using powered tool) |  | Vibration | Damage to your hands and fingers | Check the condition of anti-vibration mounts etc where fitted. Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Noise | Hearing loss | Using appropriate PPE | 1 | 1 | 1
|  |  | Kinetic Energy | Eye injury from flying debris | Using appropriate PPE | 1 | 2 | 2
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Electrical | Electrical shock due to faulty equipment or power cord. | Tool checklist and tags are implemented. | 1 | 2 | 2
16 | Cable marking |  | Communication | Wrong labeling can cause electrical shock due to wrong cirquit is energized. | Always verify the labeling with routing and schematic drawing. Continuity test for verification. | 2 | 2 | 4
Cable termination & Commissioning
17 | Cable cutting & stripping (Handsaw, cable cutter & stripping tool) |  | Penetrating sharp object | Hand injuries due to wrong handling of tool | Skilled workers to give briefing and to monitor the handling of tools. | 2 | 2 | 4
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. | 1 | 1 | 1
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work.
|  |  | Manual handling | Muscular Stress | Provide sufficient breaks during work.
18 | To install cable lug |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. Use hydraulic cable press for big cable lugs. | 1 | 1 | 1
|  |  | Mechanical | Hand injuries due to wrong handling of cable press | Skilled workers to give briefing and to monitor the handling of cable press. | 1 | 2 | 2
|  |  | Electricity | Electric shock due to wrong labeling / breaker termination or missing LOTO | Test the cable before start work. LOTO procedure. | 1 | 2 | 2
19 | Cable bending |  | Manual handling | Muscular Stress | Provide sufficient breaks during work. Provide sufficient menpower. | 1 | 1 | 1
|  |  | Electricity | Electric shock due to wrong labeling / breaker termination or missing LOTO | Test the cable before start work. LOTO procedure. | 1 | 2 | 2
20 | Termination |  | Electricity | Electric shock due to wrong labeling / breaker termination | Test the cable before start work. | 1 | 2 | 2
|  |  | Arc Flash /Arc Blast | Skin burns, damage to eyesight, Hearing loss, wounds from flying metal parts | Use of insulated tools, Test the point of termination before work, PPE, standby fire extinguisher. | 1 | 4 | 4
21 | Cable labeling |  | Communication | Wrong labeling can cause electrical shock due to wrong cirquit is energized. | Always verify the labeling with routing and schematic drawing. Continuity test for verification. | 2 | 2 | 4
22 | Energization |  | Electricity | Electric shock due to faulty equipment or cable | Test the equipment and cable before start work.Operate remotely if available.Ensure proper grounding of equipment.T&C procedure. | 1 | 2 | 2
|  |  | Heat / Cable burn | Fire due to loose termination, wrong cable specs or faulty cable | Verify the point of termination and cable specs with schematic diagram/equipment drawing.T&C procedure. | 1 | 2 | 2
|  |  | Arc Flash /Arc Blast | Skin burns, damage to eyesight, Hearing loss, wounds from flying metal parts | Use of insulated tools, T&C procedure, PPE, standby fire extinguisher.Operate remotely if available | 1 | 2 | 2
Maintenance at energized switchgear
23 | Maintenance at energized switchgear (Install additional devices & cable) |  | Electricity | Electric shock due to contact with energized parts | Use of insulated tools, appropriate PPE.Briefing on switchgear design and energized sections. Skilled workers to do the job with chargeman monitoring execution. | 1 | 4 | 4
|  |  | Arc Flash /Arc Blast | Skin burns, damage to eyesight, Hearing loss, wounds from flying metal parts | Use of insulated tools, appropriate PPE, standby fire extinguisher and pull rope.Briefing on switchgear design and energized sections. Skilled workers to do the job with chargeman monitoring execution. | 1 | 4 | 4
|  |  | Ergonomics | Fatiguen Stress and Errors, due to wokplace design. | Provide sufficient breaks during work. | 1 | 2 | 2

## MATRIX
HEXATECH | Safety Management System ( OHSAS 18001:2007 ) |  |  | Issue No. : 1 | Effective Date: 01/01/2015
| OHS Risk Rating Table |  |  | Rev. No. : 0 | Doc Ref: SMS/SF/OHSRRT
What you need to do
1. Consider what can go wrong that can hurt someone
2. Determine what the most likely outcome would be - Consequences
3. Determine how likely those consequences are - Likelihood
4. Calculate the risk rating
5. Required action
SEVERITY: | How severely could someone be hurt?
Severe | death or permanent disability to one or more persons
Major | hospital admission required
Moderate | medical treatment required
Minor | first aid required
Insignificant | injuries not requiring first aid
LIKELIHOOD: | How likely are those consequences?
Almost certain | expected to occur in most circumstances
Likely | will probably occur in most circumstances
Possible | could occur at some time
Unlikely | is not likely to occur in normal circumstances
Rare | may occur only in exceptional circumstances
LIKELIHOOD | SEVERITY
| Insignificant | Minor | Moderate | Major | Severe
| 1 | 2 | 3 | 4 | 5
Almost certain | 5 | 10 | 15 | 20 | 25
5
Likely | 4 | 8 | 12 | 16 | 20
4
Possible | 3 | 6 | 9 | 12 | 15
3
Unlikely | 2 | 4 | 6 | 8 | 10
2
Rare | 1 | 2 | 3 | 4 | 5
1
Risk level | Required action
High (15-25) | A HIGH risk requires immediate action to control the hazard as detailed in the hierarchy of control. Actions taken must be documented on the risk assessment form including date for completion.
Medium (5-12) | A MEDIUM risk requires a planned approach to controlling the hazard and applies temporary measure if required. Actions taken must be documented on the risk assessment form including date for completion.
Low (1-4) | A risk identified as LOW may be considered as acceptable and further reduction may not be necessary. However, if the risk can be resolved quickly and efficiently control measures should be implemented and recorded.