1.0	OBJECTIVE

This procedure provides installation details for internal lightings, switches, switched socket outlet

(S/S/O) with specification, quality control and Safety Plan pertaining to this project.

2.0	SCOPE

Method of installation is accordance to latest IEC, IEE, MS, JKR & TNB requirements and local authority standards.

3.0	TOOLS AND EQUIPMENT

Screw Driver, Cutter, Pliers, Knife, Wire Stripper, Ladder, Scissor Lift, Scaffolding

4.0	SAFETY & ENVIRONMENTAL PROGRAM

- All installation works will be carried-out in accordance with Project Safety Plan, Owner

Safety Procedures and statutory regulations.

- All necessary personal protective equipment will be provided and worn.

- All the tools and equipment used at site must be compliance to safety requirement.

- The site of all work activities will be kept in clean and tidy manner.

5.0	REFERENCES

MS ISO 9001: 2015 Element 7.1.6.

7.0 	WORK METHOD STATEMENT

- Internal Lighting

	Internal light fittings will be supplied and installed as specified in the submission of

approval and marked in the drawing.

	All elements of the light fittings including cable entries, diffusers etc. and connection

to the conduit where applicable should be adequately sealed as which to prevent

totally the ingress of moisture, water, vermin and insects.

	All light fittings should be adequately earthed. The earthing should be extended to the

necessary control gear where applicable.

	Its installation so that all maintenance including replacement of lamps can be carried

out from the underside of the fittings.

	All light fittings should be complete with suitable connectors for the size and number

of connections to be made at the point and the wiring required to support and/or to

connect the fittings.

b.	Switches

	Switches should be rated as for 5 or 10 amps, or more as determined by circuit load

which for inductive lighting circuit should be assessed one way or two ways as

indicated on the drawings and fixed generally at a height of 1350mm from the

finished floor level and where located in rooms the switch should, where possible be

located on the inside of the room on the handle side of the door as close to the door

as is practicable (200mm away from the door frame).

	An earthing terminal should be provided and connected to the earth continuity

conductor at every lighting switch position.

c.	Switched Socket Outlet

	Socket outlets should be generally being position 300mm above floor level for General

Office and Dry Areas or except as otherwise specified where they should be

positioned 200mm above bench in Workshop, Laboratories and etc. whichever

is applicable.

The above diagram shown the correct installation of the base box for switches & S/S/O