1.0	OBJECTIVE

This procedure provides testing details for electrical installations with specification, quality control and Safety Plan pertaining to this project.

2.0	SCOPE

Method of installation is accordance to latest IEC, IEE, MS, JKR & TNB requirements and local authority standards.

3.0	SAFETY & ENVIRONMENTAL PROGRAM

- All installation works will be carried-out in accordance with Project Safety Plan, Owner

Safety Procedures and statutory regulations.

- All necessary personal protective equipment will be provided and worn.

- All the tools and equipment used at site must be compliance to safety requirement.

- The site of all work activities will be kept in clean and tidy manner.

4.0	REFERENCES

MS ISO 9001: 2015 Element 7.1.6.

7.0 	TESTING METHOD STATEMENT

- Testing Procedure for O/C & E/F Protection Relay

General

1   Record all particulars of relay to be tested and its working settings.

2.  Change the settings to test settings where appropriate.

3.  Check that auxiliary supply voltage connected to the relay corresponds to rated auxiliary

voltage stated on its nameplate.

A.  Starting Current

1.  Connect output of test set to R (red) phase of relay.  Turn on auxiliary supply to the relay.

2.  Ensure that control know on test set has returned to zero position.

Then switch on the test set.

3.  Increase output current of test set gradually until O/C element of R (red) phase picks up.

Record the current in test form. Switch off the test set.

B.  Timing Test

1.   Connect a trip contact to timer stop terminals of the test set. A pair of voltage free

contacts are preferred.

2.  Switch on the test set, increase current to 1.3 times of setting current. Switch off the test

set with control know remaining in the same position.

3.  Switch on the test set to inject the current and start timer at the same time. After trip

contact has operated, record the relay operating time in test form. Switch off test set.

4.  Repeat steps 2 and 3 above for 2 and 3 times of setting current. Check that operating time

recorded correspond to timing characteristic of relay.

C.  High Set Element

1.  Caution: Check thermal rating of relay before high set element is tested. Ensure that

maximum allowable continuous current is not exceeded.

2.  Repeat timing test for the high set elements. Injected current shall be approximately 5%

higher than setting. In this case, the operating time will be of definite time delay instead

of inverse time characteristic.

Finally

1.   Repeat all the above test for Y (yellow), B (blue) and E/F element.

2.   Change settings back for all elements (R, Y, B & E/F) to ensure that the start currents now correspond to services settings.

3.   Disconnect all wiring between test set and relay. Check that connection to relay is normalised.

II.	Testing Procedure for Earth Leakage Relay (ELR)

1.  Record all particulars of relay to be tested and its working settings.

2.  Check that auxiliary supply voltage connected to the relay corresponds to rated

auxiliary voltage stated on its nameplate.

3.  Connect output of the test set to input terminals of ELR. Alternatively, single-phase

primary current can be injected into one of the conductors to induce a secondary

current on the ZCT.

4.  Ensure that control knob on test set has returned to zero position. Then switch on

test set.

5.  Increase the output current of test set gradually until relay picks up. Record the

current in test form.

6.  Connect a trip contact to timer stop terminals of the test set. A pair of voltage free

contacts are preferred.

7.  Switch on the test set, increase current to 2 times of setting current. Switch off the

test set with control knob remaining in the same position.

8.  Switch on the test set to inject current and start timer at the same time. After trip

contact has operated, record relay operating time in test form. Switch off test set.

9.  Disconnect all wiring between test set and relay. Check that connection to relay is

normalised.

III.	Procedure for Current Transformer Test

A)	Magnetising Characteristic

1.  Connect Secondary terminals of the CT to output terminals of a single-phase

autotransformer.

2.   An ammeter shall be connected in series with secondary winding of the CT.

3.   A voltmeter shall be connected in parallel with secondary winding of the CT.

4.   Ensure that the autotransformer is turned to zero output position.

Then switch on power supply to the autotransformer.

5.   Increase output of the autotransformer gradually. Record the voltmeter and ammeter

reading in each step until the CT saturation point is reached.

6.   At least eight readings are obtained and check that the reading obtained would enable

magnetising curve to be plotted showing its saturation voltage.

B)	Insulation Resistance of CT Secondary

1.  Check that all electronic devices such as relays, digital meters etc. in CT secondary circuit

are isolated.

2.  Remove earthing connection of CT neutral point.

3.  Identify the nearest earth point to be used as reference and ensure that it is properly

earthed.

4.  Connect one terminal of insulation tester to CT secondary and the other terminal to the

earth point stated in step 3 above.

5.  Switch insulation tester to 500V dc for 20seconds and obtain insulation resistance reading

of CT secondary.

6.  Switch off insulation tester. Discharge at CT terminal measured. Restore connection of CT

earth point and connection to other devices in CT secondary circuit.

IV.	Insulation-resistance test

1.	Tests should be carried out using the appropriate DC test voltage.

2.	Make sure the main switch is off and all fuses in place, switches and circuit-breakers

closed, lamp removed and other current-using equipment disconnected.

3.	Test should be carried out as below:

a.   Insulation resistance between live conductors

b.   Insulation resistance to earth

The table below indicates the test voltages and the minimum acceptable values of insulation resistance.

V.	Measurement of Earth Electrode Resistance