## App I
HEXATECH |  | PROJECT DEPARTMENT |  |  |  | Issue No.: 1 | Document Effective Date: 01 Mar 2017 | Page 6 of 6
|  | Method Statement For Building Electrical Maintenance - Appendix I |  |  |  | Revision No.: 0 |  | Document Ref.: MS-E019-02
APPENDIX I
TO METHOD STATEMENT MS-E019-01
LIST OF BUILDING OWNER'S ELECTRICAL EQUIPMENT
WHICH REQUIRES MAINTENANCE WORK
Building Owner's Name |  |  |  |  | Name of Building
Building Owner's Representative Name |  |  |  |  | Address of Building
ITEM | ELECTRICAL EQUIPMENT |  | MAINTENANCE WORK SPECIFICATION
1 | 11KV Electrical Switchgear |  | 1.1 | Monthly inspection by qualified HT Chargeman (Preventive Maintenance).
|  |  | 1.2 | Service VCB once every 5 years (Suruhanjaya Tenaga Requirement) (Predictive Maintenance).
2 | Transformer |  | 2.1 | Monthly inspection by qualified HT Chargeman (Preventive Maintenance).
|  |  | 2.2 | Service Transformer once every 5 years (Suruhanjaya Tenaga Requirement) (Predictive Maintenance).
3 | Generator Set |  | 3.1 | Weekly inspection & test run by qualified Chargeman (Preventive Maintenance).
|  |  | 3.2 | Service Genset - once every 2 years (subject to usage) (Predictive Maintenance).
4 | Main Switchboard (MSB) & Sub Switchboard (SSB) |  | 4.1 | Calibration of protection relay - once every two years (Preventive Maintenance).
|  |  | 4.2 | Service MSB & SSB - once every 5 years (Suruhanjaya Tenaga Requirement) (Predictive Maintenance).
5 | Busduct / Busway |  | 5.1 | Thermographic scanning to be conducted on quarterly basis (Preventive Maintenance).
|  |  | 5.2 | Check busduct/busway connectivity at joints and terminals (once every 5 years - to torque joints & terminals) (Predictive Maintenance).
6 | Distribution panel circuitary to light fittings. |  | 6.1 | Check circuit breaker and ampre used is correct for the lighting circuit (as required) (Predictive Maintenance).
|  |  | 6.2 | Check neutral and earth connections (as required) (Predictive Maintenance).
|  |  | 6.3 | Check installation and functionality of timer setting and re-correct it if necessary (as required) (Predictive Maintenance).